Electrical—Assured Equipment Grounding Conductor Program

29 CFR 1910.304—Wiring Design and Protection

Scope/Application:  This standard applies if employees will not be protected by ground fault circuit interrupters during temporary wiring installations used during construction—like activities.

Standard Requirements for 29 CFR 1910.304—Wiring Design and Protection:

- Programs/Plans: Assured Equipment Grounding Conductor Program

- Procedures/Practices/Controls:  Work procedures (Include in your Assured Equipment Grounding Conductor Program)

- Training: None required

- Inspections: Visual before use, daily

- Recordkeeping/Documentation: Program

Note: Please reference 29 CFR 1910.304—Wiring Design and Protection to ensure that all the standard requirements are being met.

29 CFR 1926.404—Wiring Design and Protection

Scope/Application: This standard applies if employees will not be protected by ground fault circuit interrupters during temporary wiring installations used during construction—like activities.

Standard Requirements for 29 CFR 1926.404—Wiring Design and Protection:

- Programs/Plans: Assured Equipment Grounding Conductor Program

- Procedures/Practices: Work procedures (Include in your Assured Equipment Grounding Conductor Program)

- Training: Initially (Reference 29 CFR 1926.21)

- Inspections: Visual before use, daily

- Documentation: Program

Note: Please reference 29 CFR 1926.404—Wiring Design and Protection to ensure that all the standard requirements are being met.

Example Program: The following example program should be modified to be site-specific to your organization.

Electrical—Assured Equipment Grounding Conductor Program

Whenever an Assured Equipment Grounding Conductor Program (AEGCP) is used in place of ground-fault circuit interrupters (GFCI) for ground-fault protection, the following requirements will be followed:

Written description of the program at the jobsite.

_______________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

The following specific procedures will be used for the required equipment inspections, tests, and test schedule. These will be made available to OSHA and to affected persons upon demand.

______________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

The following designated competent person(s) will implement the program.  OSHA defines a competent person as someone who is a) qualified to identify hazards, and b) authorized to take prompt corrective measures.

_______________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

All cord sets, attachment caps, plugs and receptacles, and any equipment connected by cord and plug, will be visually inspected before use each day. If any external damage is seen, such as deformed or missing pins, damaged insulation, etc., or discover internal damage, the equipment is to be taken out of use until it is repaired.

Two OSHA-required tests will be performed on all electrical equipment: a continuity test, and a terminal connection test. These tests are required:

- Before first use.

- After any repairs, and before placing back in service.

- After suspected damage, and before returning to use.

- Every 3 months.

We will maintain a written record (Example below) of the required tests, identifying all equipment that passed the test and the last date it was tested (or the testing interval). The most current record will be maintained. These records will be readily available to OSHA and affected persons upon demand.

Electrical—Assured Equipment Grounding Conductor Test Record

Date of Current Test:___________    Date of Last Test:______________

Testing Interval (If applicable): _____________________________

Equipment Tested:

______________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Test Completed:

Continuity Test: ___  			Pass / Fail

Terminal Connection Test:___		Pass / Fail

Reason for Test (Please check):

Initial Use:____         After Repair: ____ 		After Damage: _____		Three Month: _____

Other: ________________________________________________________________________________________

A written record of the required tests, identifying all equipment that passed the test and the last date it was tested (or the testing interval) will be maintained. These records will be readily available to OSHA and affected persons upon demand.

Signature:_____________________________________________________________________________________

Free Outreach Resources:

Safety and Health Programs and Plans (i.e., Example Programs to be Made Site-Specific)

A - Z Safety and Health Topics (i.e., Learn More About Safety and Health Topics)

Which Standards Apply? (Identify the Standards Applicable to Your Worksite)

Safety and Health Presentations (Downloadable Presentations to be Made Site-Specific)

OSH Training Calendar (i.e., Register for Webinars, In-Person Classroom Training, Virtual Events)

Streaming Video Services (On-Demand Training)

Request Outreach Services (i.e., Request Training, Booths, Guest Speaker)

AskOSH (Interpretations)